## Adlar 6kW
Warmtepom Adlar Cadastra Aurora 2 6kw
L0 | 0 | Compressor manual control 90=auto 1=manual) | P00 | 0 | Ambient temp sensor T1 | P50 | 10 | cooling target freq constant A | P100 | 65 | PWM pump min speed | P150 | 2 | secondary heating pump selection | P200 | 25 | C2 working condition fan freq | P250 | 4 | Target overheat of main valve under low water temperature conditions
L1 | 0 | Compressor target frequency (0-120Hz) | P01 | 0 | high volt switch / high pressure | P51 | 30 | minimum freq limit for refrigeration | P101 | 1 | pump control methode (0=AC 1=DC) | P151 | 0 | hot water heat source return | P201 | 45 | B2 working condition fan freq | P251 | 5 | PFC shutdown current
L2 | 0 | Manual fan Control (0=auto 1=manual) | P02 | 0 | low volt switch / low pressure | P52 | 70 | upper limit of target freq of refrigeration | P102 | 0 | 4-way valve control mode | P152 | 1 | heating heat source difference | P202 | 55 | A2 working condition fan freq | P252 | 3 | Target overheat of main valve under high water temperature rated conditions
L3 | 0 | Fan target frequency (0-70 (P06=1) | P03 | 0 | water flow switch (1=disable) | P53 | 42 | lower limit target freq refrigeration | P103 | 3 | mode switching min run time | P153 | 70 | hot water heat source combined upper limit | P203 | 55 | F2 working condition fan freq | P253 | 6 | PFC turn-on current
L4 | 0 | Electronic expansion valve manually controlled (0=auto 1=manual) | P04 | 1 | thermal overload switch | P54 | 85 | heating target freq constant B | P104 | 25 | mode switching percentage of operating freq | P154 | 60 | heating heat source combined temperature ceiling | P204 | 1 | D1 working condition main valve target overheat | P254 | 0 | Heating medium (0=water)
L5 | 0 | Electronic expansion valve target number steps (0-480p) | P05 | 0 | linkage switch (1=disable) | P55 | 85 | upper limit of heating target freq | P105 | 15 | Cooling mode operating temp limit | P155 | 0 | compressor code selection | P205 | 1 | C1 working condition main valve target overheat | P255 | 1 | smart grid options (1=disable)
L6 | 0 | EVI manual control (0=auto 1=manual) | P06 | 1 | fan type settings | P56 | 50 | lower limit heating target freq | P106 | 40 | heating mode operation limit | P156 | 0 | Aux electronic expansion valve (0=enable) | P206 | 2 | B1 working condition main valve target overheat | P256 | 30 | smart grid optins peak grid running time
L7 | 0 | EVI target steps (0-480P) | P07 | 0 | high volt protection lock | P57 | 20 | minimum heating freq 1 | P107 | 55 | hot water mode opeating temp limit | P157 | 0 | Aux electronic expansion valve to reduce the temperature differential | P207 | 2 | A1 working condition main valve target overheat | P257 | 2 | dual temperature zone selection
L8 | 0 | DC water pump control (0=auto 1=manual) | P08 | 0 | low volt protection lock | P58 | 35 | minimum heating freq 2 | P108 | 55 | hot water setting temp limit | P158 | -15 | heating limit water temp and starting ambient temp\ | P208 | 2 | F1 working condition main valve target overheat | P258 | 7 | mixed water regulating valve cycle
L9 | 0 | DC water flow autput (0-100) (0=min 100=max) | P09 | 0 | exhaust protection lock | P59 | 40 | minimum heating freq 3 | P109 | 20 | Hot water setting lower temp limit | P159 | 68 | temperature limit constant A | P209 | 2 | D2 working condition main valve target overheat | P259 | 120 | mixing valve full cycle time
L10 | 0 | PFC manual control (0=auto 1=off 2=on) | P10 | 0 | waterflow switch lock | P60 | 85 | hot water target freq constants | P110 | 55 | heating setting temp limit | P160 | 14 | temperature limit coefficient B | P210 | 2 | C2 working condition main valve target overheat | P260 | 99 | maximum water pump speed
L11 | 30 | ?? | P11 | 65 | high volt/pressure protection value | P61 | 85 | upper limit freq hot water | P111 | 20 | lower temp limit for heating | P161 | 0 | aux pump selection | P211 | 2 | B2 working condition main valve target overheat | P261 | 30 | water pump speed at constant temp
L12 | 1 | high temperatur sterilization funct (0=auto 1=disable 2=manual) | P12 | 59 | high volt freq value | P62 | 50 | lower limit freq hot water | P112 | 25 | upper temp limit for refrigeration | P162 | 0 | hot water line antifreeze interval (0=disabled) | P212 | 2 | A2 working condition main valve target overheat | P262 | 1 | testing mode (on/off)
L13 | 7 | number of days between sterilization (5-30) | P13 | -40 | low voltage protection value | P63 | 40 | min freq hot water 1 | P113 | 7 | lower temp limit refrigeration | P163 | 19 | pump speed regulation minimum flow | P213 | 2 | F2 working condition main valve target overheat | P263 | 3 | freq increase time - exit exhaust overheat time
L14 | 23 | Sterilization start time (00:00-24:00) | P14 | -35 | low voltage freq limit value | P64 | 40 | min freq hot water 2 | P114 | 1 | number of presses selected (1=single) | P164 | 3 | energy level control | P214 | 130 | D1 working condition initial opening of main valve | P264 | 100 | percentage correction for main valve opening - running at initial freq
L15 | 10 | Sterilization run time (0-50 min) | P15 | 115 | exhaust temp protection value | P65 | 45 | min freq hot water 3 | P115 | 1 | model selection | P165 | 3 | load the difference | P215 | 90 | C1 working condition initial opening of main valve | P265 | 1 | percentage of mixing valve adjustment
L16 | 70 | sterilization temperature (50-80) | P16 | 95 | exhaust temp freq limit | P66 | 40 | DC fan inition freq | P116 | 1 | unit temp comtrol mode (0=return water 1= water outlet) | P166 | 2 | load shedding differential | P216 | 100 | B1 working condition initial opening of main valve | P266 | 0 | dual temp zone mode selection
L17 | 1 | Water level control (0=disabled 1=high low 2=high high low) | P17 | 37 | refrigeration fan lift value | P67 | 20 | DC fan heating min freq | P117 | 5 | antifreeze enters ring temp | P167 | 3 | emergency stop difference | P217 | 150 | A1 working condition initial opening of main valve | P267 | 5 | dual temp zone control return temp
L18 | 1 | hydration control | P18 | 32 | refrigeration fan speed reduction value | P68 | 50 | DC fan heating max freq | P118 | 3 | antifreeze ingress temp T15 | P168 | 50 | hot water mode start-up ratio | P218 | 130 | F1 working condition initial opening of main valve | P268 | 1
L19 | 45 | Allow water temperature | P19 | 12 | speed reduction value of heating fan | P69 | 20 | DC fan cooling min freq | P119 | 2 | type of regrigerant (2=R32 3=R290) | P169 | 100 | non-hot water mode start-up ratio | P219 | 110 | D2 working condition initial opening of main valve
L20 | 5 | Hysteresis of replenishment water temperature | P20 | 8 | heating fan lift value | P70 | 55 | DC fan cooling max freq | P120 | 1 | anti condensation function (1=disable) | P170 | 7 | load cycle | P220 | 85 | C2 working condition initial opening of main valve
L21 | 1 | low water cut-off opweration (0=not start 1=power on not start 2=start) | P21 | -26 | unit is prohibited from starting low temperature (host) | P71 | 45 | compressor freq allow aux valve and EVI to open | P121 | 0 | low value heating freq shield 1 | P171 | -30 | shield low voltage switch ring temp value | P221 | 90 | B2 working condition initial opening of main valve
L22 | 0 | backwater mode (host) (0=disabled 1= cont return water 2=cycle return water 3= temp diff return water) | P22 | -15 | electric heating start-up ambient temp (host) | P72 | 35 | compressor freq allow aux valve and EVI to close | P122 | 0 | high value heating freq shield 1 | P172 | 65 | heating DC fan target freq constant c | P222 | 120 | A2 working condition initial opening of main valve
L23 | 40 | inlet water temperature T8 (host) (20-65) | P23 | 12 | temp difference between inlet and outlet is too large | P73 | 400 | Cooling main valve initial opening 1 | P123 | 0 | low value heating freq shield 2 | P173 | 40 | heating fan minimum target freq | P223 | 100 | F2 working condition initial opening of main valve
L24 | 5 | return water hysteresis (1-15) | P24 | 2 | inlet water temp T8 compensation value | P74 | 300 | Cooling main valve initial opening 2 | P124 | 0 | high value heating freq shield 2 | P174 | 450 | defrost opening | P224 | 2 | D1 working condition aux valve target overheat
L25 | 30 | backwater cycle (host) (3-90) | P25 | 2 | outlet temp T15 compensation value | P75 | 350 | Cooling main valve initial opening 3 | P125 | 0 | low value heating freq shield 3 | P175 | 10 | pump interval cycle unit shutdown at constant temp | P225 | 2 | C1 working condition aux valve target overheat
L26 | 5 | return time (host) (1-30) | P26 | 0 | Heating/ airco differential value | P76 | 100 | Cooling main valve minimum opening | P126 | 0 | high value heating freq shield 3 | P176 | 0 | compressor minimum run time in defrost | P226 | 2 | B1 working condition aux valve target overheat
L27 | 1 | 1=HL8 / 0 =cumstom stooklijn | P27 | 0 | floor heating difference | P77 | 40 | Heating main valve minimum opening | P127 | 0 | low value cooling freq shield 1 | P177 | 40 | defrost freq setting value in different water temp | P227 | 2 | A1 working condition aux valve target overheat
L28 | -5 | daling per 10grden buitentemp / custom stooklijn | P28 | 1 | pump control when temp is stopped | P78 | 480 | Main valve maximum opening | P128 | 0 | high value cooling freq shield 1 | P178 | 70 | defrost freq high water temp | P228 | 2 | F1 working condition aux valve target overheat
L29 | 55 | doel temp bij -15 graden | P29 | 2 | anti freeze pump operation time (every 10 min) | P79 | 80 | main valve initial opening constanc C | P129 | 0 | low value cooling freq shield 2 | P179 | 15 | target freq power mode | P229 | 2 | D2 working condition aux valve target overheat
|  |  | P30 | 0 | defrost mode selection (0=smart 1=time 2=fast) | P80 | 60 | Main valve initial opening coefficient A | P130 | 0 | high value cooling freq shield 2 | P180 | 5 | target freq upper limit - power mode | P230 | 2 | C2 working condition aux valve target overheat
|  |  | P31 | 45 | cumulative run time threshold for defrosting | P81 | 40 | Main valve initial opening coefficient B | P131 | 0 | low value cooling freq shield 3 | P181 | 0 | defrost selection evaporate side (0=current 1=heating 2=DHW | P231 | 2 | B2 working condition aux valve target overheat
|  |  | P32 | -5 | defrost coil temperature | P82 | 480 | Aux valve Max opening degree | P132 | 0 | high value cooling freq shield 3 | P182 | 3 | pipe electric heating option (3=disabled) | P232 | 2 | A2 working condition aux valve target overheat
|  |  | P33 | 9 | defrost temp difference 1 | P83 | 30 | Aux valve minimum opening degree | P133 | 0 | fan module ( 0=integral) | P183 | 998 | parameter password setting (0=disable) | P233 | 2 | F2 working condition aux valve target overheat
|  |  | P34 | 9 | defrost temp difference 2 | P84 | 40 | main valve adjustment period | P134 | 10 | water flow is too low protection limit | P184 | 25 | D1 working condition compressor freq | P234 | 125 | D1 working condition initial opening of aux valve
|  |  | P35 | 10 | max defrost time | P85 | 50 | Auux valve initial open degree C | P135 | 5 | anti condensation starts temp difference | P185 | 25 | C1 working condition compressor freq | P235 | 85 | C1 working condition initial opening of aux valve
|  |  | P36 | 12 | exit defrost coil temp | P86 | 30 | Aux valve initial open degree A | P136 | 25 | throttle bypass valve opens ring temp | P186 | 39 | B1 working condition compressor freq | P236 | 35 | B1 working condition initial opening of aux valve
|  |  | P37 | 0 | darwin shitdown mode | P87 | 20 | Aux valve initial open degree B | P137 | 0 | throttled bypass delay press | P187 | 78 | A1 working condition compressor freq | P237 | 65 | A1 working condition initial opening of aux valve
|  |  | P38 | 300 | opening degree main valve (-999 - 999) | P88 | 50 | silent heat compressor max freq | P138 | 70 | defrosting press freq | P188 | 85 | F1 working condition compressor freq | P238 | 85 | F1 working condition initial opening of aux valve
|  |  | P39 | 0 | Pressure sensor setting | P89 | 40 | silent heat fan max freq | P139 | 0 | Air conditioning electric heating otion | P189 | 25 | D2 working condition compressor freq | P239 | 140 | D2 working condition initial opening of aux valve
|  |  | P40 | -2 | cooling target overheat correction valve | P90 | 23 | Ambient temp allow aux and EVI to open | P140 | 1 | hot water electric heating option | P190 | 25 | C2 working condition compressor freq | P240 | 330 | C2 working condition initial opening of aux valve
|  |  | P41 | 2 | heating high pressure and freq limit correction value | P91 | 3 | interval period allow aux and EVI to open | P141 | 5 | dew point duration of defrosting | P191 | 39 | B2 working condition compressor freq | P241 | 200 | B2 working condition initial opening of aux valve
|  |  | P42 | -1 | heating target overheat correction value | P92 | 2 | Temp diffential T8-T7 - Allow aux and EVI to open | P142 | 11 | dew point constant for defrosting | P192 | 78 | A2 working condition compressor freq | P242 | 350 | A2 working condition initial opening of aux valve
|  |  | P43 | 0 | medium voltage switch setting | P93 | 1 | Compressor running time Allow aux and EVI to open | P143 | 7 | defrosting can enter the water temperature | P193 | 85 | F2 working condition compressor freq | P243 | 350 | F2 working condition initial opening of aux valve
|  |  | P44 | 0 | water flow switch failure detection setup | P94 | 40 | Aux valve adjustment cycle | P144 | 17 | defrosting can enter ring temperature | P194 | 25 | D1 working condition fan freq | P244 | 22 | Target water flow in low water temperature conditions
|  |  | P45 | 1 | messaging address code | P95 | 0 | Network pump operation mode (0=total 1=independent) | P145 | -30 | effluent antifreeze protection value | P195 | 25 | C1 working condition fan freq | P245 | 15 | Target water flow under high water temperature conditions
|  |  | P46 | 8 | return differential liquid injection solenoid valve opening | P96 | 5 | Hot water return difference | P146 | 35 | pump range setpoint | P196 | 45 | B1 working condition fan freq | P246 | 50 | low water temperature rated fan freq
|  |  | P47 | 1 | EVI target overheat constant | P97 | 0 | Hot water tank temp manual compensation value | P147 | 2 | refrigeration and antifreeze methode | P197 | 55 | A1 working condition fan freq | P247 | 220 | initial opening of main valve under low water temp rated conditions
|  |  | P48 | 1 | enable hot water tank temp sensor | P98 | 0 | Hot water tank temp auto compensation value | P148 | 1 | refrigeration anti freeze temp value | P198 | 55 | F1 working condition fan freq | P248 | 50 | high water temperature rated fan freq
|  |  | P49 | 30 | hot water freq running percentage | P99 | 5 | Water pump speed regulation temperature difference | P149 | 58 | effluent is too high | P199 | 25 | D2 working condition fan freq | P249 | 170 | initial opening of main valve under high water temp rated conditions